## Sheet3
REGC_C |  | REEC_C
Value | Model CONS | Value | Variable
999 | Iqrmax (pu/s), maximum rate limit on Iqcmd (> 0) | 0.7 | Vdip (pu), low voltage threshold for reactive current injection
-999 | Iqrmin (pu/s), maximum rate limit on Iqcmd (< 0) | 1.3 | Vup (pu), high voltage threshold for reactive current injection
0.02 | Tfltr (s), terminal voltage filter constant | 0.02 | Trv (s), Voltage filter time constant
10 | rrpwr (pu/s), rate of recovery of active current or power (>0) | 0 | dbd1 (pu), Voltage error dead band lower threshold (<=0)
1 | Imax (pu), Maximum converter current rating (> 0) | 0 | dbd2 (pu), Voltage error dead band upper threshold (>=0)
0.0083 | Te (s), delay in converter control (> 0) | 3 | Kqv (pu), Reactive current injection gain
0.5 | Kip (pu/pu), Inner current control loop proportional gain | 1 | Iqhl (pu), Upper limit on reactive current injection Iqinj
20 | Kii (pu/(pu*s)), Inner current control loop integral gain | -1 | Iqll (pu), Lower limit on reactive current injection Iqinj
20 | Kppll (pu/pu), PLL proportional gain | 0 | Vref0 (pu), User defined reference (if 0, initialized by model)
700 | Kipll (pu/(pu*s)), PLL integral gain | 0.02 | Tp (s), Filter time constant for electrical power
75 | wmax (rad/s), upper PLL rate limit | 0.5 | QMax (pu), limit for reactive power regulator
-75 | Wmin (rad/s), lower PLL rate limit | -0.5 | QMin (pu) limit for reactive power regulator
0.7 | Vpllfrz (pu), voltage below which PLL state s7 is frozen | 1.3 | VMAX (pu), Max. limit for voltage control
|  | 0.7 | VMIN (pu), Min. limit for voltage control
|  | 1.2 | Kqp (pu), Reactive power regulator proportional gain
Value | Model ICONS | 1.9 | Kqi (pu), Reactive power regulator integral gain
1 | RateFlag, 0: rate limit on Ipcmd, 1: rate limit on active power | 1 | Kvp (pu), Voltage regulator proportional gain
1 | PQ-priority Flag, 0: Q-priority, 1: P-priority | 1.1 | Kvi (pu), Voltage regulator integral gain
|  | 0.02 | Tiq (s), Time constant on delay s4
|  | 99 | dPmax (pu/s) (>0) Power reference max. ramprate
|  | -99 | dPmin (pu/s) (<0) Power reference min. ramprate
|  | 1 | PMAX (pu), Max. power limit
|  | -1 | PMIN (pu), Min. power limit
|  | 1.3 | Imax (pu), Maximum allowable total converter current limit
|  | 0.02 | Tpord (s), Power filter time constant
|  | 0 | Vq1 (pu), Reactive Power V-I pair, voltage
|  | 0 | Iq1 (pu), Reactive Power V-I pair, current
|  | 0 | Vq2 (pu) (Vq2>Vq1), Reactive Power V-I pair, voltage
|  | 0 | Iq2 (pu) (Iq2>=Iq1), Reactive Power V-I pair, current
|  | 0 | Vq3 (pu) (Vq3>Vq2), Reactive Power V-I pair, voltage
|  | 0 | Iq3 (pu) (Iq3>=Iq2), Reactive Power V-I pair, current
|  | 0 | Vq4 (pu) (Vq4>Vq3), Reactive Power V-I pair, voltage
|  | 0 | Iq4 (pu) (Iq4>=Iq3), Reactive Power V-I pair, current
|  | 0 | Vp1 (pu), Real Power V-I pair, voltage
|  | 0 | Ip1 (pu), Real Power V-I pair, current
|  | 0 | Vp2 (pu) (Vp2>Vp1), Real Power V-I pair, voltage
|  | 0 | Ip2 (pu) (Ip2>=Ip1), Real Power V-I pair, current
|  | 0 | Vp3 (pu) (Vp3>Vp2), Real Power V-I pair, voltage
|  | 0 | Ip3 (pu) (Ip3>=Ip2), Real Power V-I pair, current
|  | 0 | Vp4 (pu) (Vp4>Vp3), Real Power V-I pair, voltage
|  | 0 | Ip4 (pu) (Ip4>=Ip3), Real Power V-I pair, current
|  | 10000 | T (s), Battery discharge time (>0)
|  | 0.2 | SOCini (pu), Initial state of charge
|  | 1 | SOCmax (pu), Maximum allowable state of charge
|  | 0 | SOCmin (pu), Minimum allowable state of charge
|  | Value | Model ICONs
|  | 0 | Input this as 0. For remote bus control use the plant controller model
|  | 0 | PFFLAG (Power factor flag): 1 - power factor control; 0: Q control
|  | 1 | VFLAG: 1 if Q control; 0 voltage control
|  | 1 | QFLAG: 1 if voltage/Q control; 0 if pf/Q control
|  | 1 | PQFLAG: 1 for P priority, 0 for Q priority